BOILER HOUSE AUDIT REPORT

Lactalis - Bonnievale

Report No.: 2025 - xyz

REPORT ON

BOILER HOUSE AUDIT AT

LACTALIS PORT ELIZABETH

Report No. : 2022-xyz

Distribution

Werner Vermeulen	(email)	-	1

Ludvig Botha		(email)	-	1

Arij Reijnsburger	(email)	-	1

Master File				-	1

Prepared by:

Ludvig Botha

Service Engineer

Limit of Liability / Disclaimer

This report is limited to the matters stated herein and is not to be read as extending by implication to any other matters not specifically referred to herein.  It is addressed to and is for the use and benefit of yourselves solely and may not be disclosed or communicated to, or relied upon by, any other person, firm, or corporation without our prior written consent.

The information appearing in this report is made available to you without any representation or warranty whatsoever, whether express or implied.

ACTOM (Pty) Ltd accepts no liability whatsoever for any loss, whether direct, indirect, or consequential, including without being limited to any loss of profit, or special damages arising from information made available to you in this report and actions or transactions resulting therefrom.

This “limit of liability/disclaimer” shall be governed by and construed according to the laws of the Republic of South Africa.

Confidentiality

This report is issued as per the distribution list only and may not be copied to any other parties without the expressed permission of the author.

EXECUTIVE SUMMARY

John Thompson was requested to perform a boiler house audit at Lactalis - Bonnievale on 08/08/2025. The audit consisted of a visual inspection of the boiler, testing of safety devices, testing of boiler controls and a general inspection of the boiler house and steam reticulation system.

Due to plant demand and scheduled shutdown, it was not possible to perform any efficiency testing.

The following actions are recommended to improve compliance of the boiler house with statutory regulations and to improve the operation and thermal efficiency of the boiler plant:

Statutory compliance:

- Describe the level of compliance in relation to the annual statutory external inspection and the three-yearly statutory internal inspection.

Training:

- All boiler operators, maintenance staff and supervisors should attend an OEM training course to improve their operating and maintenance skills.

Instrumentation and controls:

- Bring boiler control panels up to the original standard or upgrade to the latest safety standard.  Various faults were observed in the panels i.e. no automatic control possible of the boiler and critical water level alarms and cut-outs don’t work. Install critical OEM instrumentation on the boiler to enable the measurement and recording of critical parameters for optimal boiler efficiency and performance.

- Calibrate exit gas temperature gauges on the boiler to indicate the level of fouling on either the waterside or the gas-side.

- Install differential pressure gauges on the grit collector to measure the pressure drop across the grit collector to determine the level of fouling.

Fuel handling:

- Overhead coal hopper with swinging chute on the boiler is installed to prevent segregation of the fuel on the stoker mat.  This will improve the combustion of fuel and thermal efficiency of the boiler.

Stoker:

- The stoker needs extensive repairs or replacement to enable reliable operation and prevent further failures and downtime of the plant.

Boiler:

- Attend to all leaks (smoke box doors, stoker side seals, emergency de-ashing doors, soot blower connections and ash ports) as air leakage reduces the overall thermal efficiency of the boiler.

- Clean boiler tubes every 3 months by brush or high-pressure water cleaning. This will ensure optimum heat transfer to the waterside resulting in improved overall thermal efficiency of the boiler.

- Regularly grease stoker front shaft bearings, sootblowers and other items with the correct grease to ensure reliable operation of the equipment.

Back-end equipment:

- The grit collector should be checked for internal blockage or wear of cyclones and cones which will reduce the efficiency of particulate collection.

- The grit collector should be checked for ingress of air through inspection hatches or the double-flap valve.  It is important that an airtight seal is always maintained for optimum performance of the grit collector.

- The boiler needs a back-end upgrade to increase the efficiency of particulate collection.

Condensate recovery:

- The return of condensate from the plant should be automated to prevent the loss of condensate from the feedwater storage tank overflows.

- The condensate lines and feedwater storage tank should be lagged and clad to prevent the loss of energy.

Record keeping:

- Record all boiler data on the boiler log sheet during operation including soot blowing and water level testing.

# OBJECTIVE

John Thompson was requested to perform a boiler house audit at Moroil, Mauritius and to give recommendations to remedy the shortcomings.

# SCOPE OF WORK

An audit was conducted on the John Thompson coal-fired boiler with serial number 72697 as follows:

- Check the AIA inspection records.

- Check the level of automation of the boiler.

- Check the condition of the instrumentation on the boiler.

- Check the mechanical condition of boiler, stoker and ancillary equipment.

- Check the condition of the steam lines and steam trap sets within the boiler house.

- Check the quality of the boiler logbook kept by the boiler operators and supervisors.

- Check the boiler water softener and chemical dosing plant and the operation thereof.

- Check the combustion settings in relation to flue gas analysis, exit gas temperature, coal bed thickness and coal bed length; and

- Check the level of attention the boiler operator staff give to combustion settings and normal boiler duties

# DESCRIPTION OF BOILER PLANT

The boiler plant consists of one John Thompson package boiler. Boiler 72697 is coal-fired. Steam from the boiler plant is used in the processing plant. The boiler operating pressure is set at 13.5 bar(g).

The coal is offloaded in the coal storage area and is transferred via an inclined screw conveyor to the stoker hoppers.

There is a submerged belt ash conveyor to remove the ash to an ash skip.

The coal boiler has a boiler-mounted ID fan and is connected to a guyed chimney stack.

The boiler has a OEM boiler control panel with various faults.

# STEAM SYSTEM PROFILING

## FINDINGS

- The boiler is not fitted with a steam flow meter.

- The feed water flow rate to the boiler is recorded and trend graphs are not available.

- The make-up water flow rate is recorded, and no trend graphs are available.

- The condensate return flow rate is not calculated and no trend graphs are available.

- The fuel consumption is not monitored.

## RECOMMENDATIONS

It is critical to monitor all inputs in the production of steam.  Any variations should be investigated.

The following should be measured and/or calculated and recorded:

- Steam production

- Fuel flow rate

- Feed water flow rate

- Make-up water flow rate

- Blowdown flow rate

- Chemical input flow rate

- Condensate return flow rate and temperature

It is also recommended to benchmark the amount of steam required per unit of product and track this value continuously.

# STEAM SYSTEM OPERATING PRACTICES

## STEAM TRAPS

### FINDINGS

- Steam traps are installed on the steam lines in the boiler house and on the steam lines to the process.

- The steam trap sets consist of an isolation valve before the steam trap.

- Most of the steam traps are functional but some are passing steam as can be seen from the feedwater storage tank overfilling and the flow of steam from the feedwater storage tank vent.

### RECOMMENDATIONS

- Carry out an in-house audit to determine:

  - Whether the correct steam traps have been selected for the application

  - Whether the steam traps are correctly sized

- Replace damaged traps. It is recommended that the steam trap set consists of the following:

  - Two isolation valves, one on either side of the trap set

  - Strainer before steam trap

  - Steam trap

  - Sight glass

  - Check valve

- Set up and maintain a steam trap database.

- Steam traps should be tested at least once a year and all maintenance should be recorded.

- All condensate return pipework should be lagged and clad and returned to the feedwater storage tank.

- Installation of bypass valves to allow contaminated condensate to be dumped.

## WATER TREATMENT

### FINDINGS

- The boiler waterside was not inspected.

- Make-up water is not being softened as the unit is not working. Customer to supply service report.

- TDS and pH are not measured and recorded daily.

- Boiler does not have automatic TDS control.

- Water treatment service reports need to be supplied for review.

- Chemical dosing pumps are installed for boiler and chemical are introduced into the feed water storage tank. Every time a feed water pump runs chemicals are injected into the feedwater storage tank.

- Regular inspection of the chemical drums is required and must be noted in the operator’s logbook to prevent the boiler being operated without the required chemicals which will be detrimental to the boiler.

- A local water treatment specialist must make regular visits to the boiler house to ensure that the operators and laboratory technicians maintain the correct chemical dosing and boiler blowdown.

- Chemical spillage is present on feedwater storage tank and pipework.

### RECOMMENDATIONS

- Repair or replace the water softener unit.

- Automatic TDS controls and water sample coolers needs to be installed on the boiler.

- TDS levels must be maintained between 2500-3000 ppm to prevent water carry-over to the process.

- TDS and pH levels must be recorded for each shift in the daily logbook.

## INSULATION

### FINDINGS

- Steam pipework inside the boiler house is lagged and clad.

- Valves and flanges inside the boiler house are unlagged.

- Boiler feedwater storage tank is lagged and clad with signs of spillage and wear.

- Condensate return pipework is unlagged on some return lines.

### RECOMMENDATIONS

- Repair all damaged lagging and cladding.

- Lag all unlagged pipework, valves, and flanges inside the boiler house.

- Lag the steam pipework to each process.

- Lag valves and flanges between boiler house and process plants.

- Lag feedwater storage tank.

- Lag the condensate return pipework.

## STEAM LEAKS

### FINDINGS

The following steam leaks were noted:

- There was damage to the boiler integral pipework.

- The blowdown lines were leaking.

### RECOMMENDATIONS

- Replace and repair leaking valves and components as soon as steam and water leaks occur.

## MAINTENANCE

### FINDINGS

- The boilers are subjected to an internal and external inspection annually as required by law.

- The AIA hot commissioning report for the setting of safety limiters could not be provided for review.

- Weekly or monthly maintenance schedules could not be provided for review.

- The boiler ash chute did not maintain an air-tight seal and must be repaired. This negatively affects boiler efficiency.

- The grit collector double-flap valve did not maintain an air-tight seal. This negatively affects the grit arrestor efficiency.

- The grit collector trolley was in a poor state of repair and needs replacement.

- The smoke box doors did not maintain an air-tight seal.  This negatively affects the boiler efficiency.

### 4.5.2   RECOMMENDATIONS

- Repair and replace leaking components.

- Repair and replace damaged components.

- Calibrate boiler instrumentation.

- Implement daily, weekly and monthly maintenance schedules for the boiler plant, steam distribution and condensate recovery equipment.

- Record all maintenance.

# BOILER PLANT OPERATING PRACTICES

## BOILER WATER LEVEL

### FINDINGS

- Gauge glasses are not blown down.

- Alarms for

  - Low level – Only audible and no visual (BS cut-out with auto-restart once the water level is corrected; EN lock-out requiring manual restart)

  - Extra low level – No separate audible alarm only visual (BS and EN lock-out requiring manual restart)

  - No indication or record is kept of actual level of water limiters.

- Records of alarm tests could not be provided for review.

### RECOMMENDATIONS

- The gauge glasses should be blown down once per shift to ensure that they are working correctly and that the standpipes do not become blocked with scale.

- Mobrey level switches should be blown down once per shift to ensure that they are working correctly and that the standpipes do not become blocked with scale.

- All alarms, audible and visual, should be recorded. If the water level in the gauge glasses is correct and a low water alarm persists, the Mobreys should be checked for correct operation. If the water level remains low the pumps should be checked.

- Urgent attention should be paid to the operation of all water level controls.

- Urgent attention should be paid to malfunctioning boiler feedwater pumps.

- Cabling to water level switches and/or transmitters is not secure and safe.

## RECOVERY AND UTILISATION OF AVAILABLE CONDENSATE

### FINDINGS

- A condensate recovery and utilisation audit should be conducted to maximise condensate/heat recovery.

### RECOMMENDATIONS

- Automate the condensate return system.

- Check all steam traps to ensure that they are not passing steam.

## COMBUSTION

### FINDINGS

- Fuel analysis records could not be provided for review.

- The boiler has a pressure drop of 980 Pa.

- The grit arrestor pressure drop is 680 Pa.

- Incomplete combustion of fuel was occurring with red coals being discharged off the end of the stoker.

- The stoker mats show signs of overheating with damaged links and bent link rods.

- The draught pipework to ignition arches was damaged and bent which negatively affects the speed of reaction of combustion control.

- The fireside should be cleaned on a regular basis (every three to four months) to allow for optimum heat transfer.

- The stokers need to be levelled in the boiler. The stoker frames show signs of being distorted.

- Further inspection of the stokers revealed the following:

- Non-OEM parts were being used.

- The stoker side seals and intermediate blocks were incorrectly assembled.

- The guillotine door was level.

- The guillotine door castings / refractory was damaged.

- The guillotine door height was not displayed.

- The stoker hoppers and shut off doors need replacement.

- The ends of the link rod were damaged with indication of drifting rods and missing split pins.

- Incorrectly installed stokers which will lead to failures and down-time.

### RECOMMENDATIONS

- Perform a proximate analysis, a mineral ash analysis and ash fusion temperatures at least once per month to ensure that the correct grade of fuel is being supplied.

- Ensure that the volatile content of fuel is within specification.

- Fuel with a low ash fusion temperature will result in clinker formation on the chain grate which reduces the overall thermal efficiency of the boiler by preventing the flow of combustion air to the fuel.

- Slagging (birds nesting) occurs when molten particles carried in the gas stream strike the tubeplate surface where they cool and solidify and restrict the flow of gas through the boiler.

- Install oxygen probes and analysers.

- Reduce the flue gas oxygen content to 8% by adjusting the fuel trim and by automating the under grate dampers.

- Introduce moisturising steam into the coal in the stoker hopper.  This assists the fine fuel particles to stick to the larger fuel particles and to be combusted instead of being blown through the boiler.

- Close spyholes and air leaks around the stoker to prevent cold air cooling the ignition arch and reducing the ignition of the fuel which could result in poor combustion.

- It is recommended that the customer installs new stokers with swinging chutes.

- Replace boiler control panel with a fully automated system that is locally supported complete with operating manuals. This system must be compliant with the Pressure Equipment Regulations and the EN boiler safety standards.

- Operators must be trained to safely operate the equipment.

## OPERATOR DUTIES

### FINDINGS

- Blowdown of gauge glasses is not done regularly.

- Soot blowing is not done regularly.

The following needs to be recorded every 4-hour:

- Boiler water TDS

- Boiler water pH

- Blowdown (yes/no)

- Feedwater TDS

- Feedwater pH

- Feedwater hardness

- Feedwater pressure

- Feedwater storage tank level

- Softener online (1-2)

- Bags of salt added

- Brine tank level

- Stack appearance (0 – invisible, 1 – visible but very slight, 2 – clearly visible)

- Ignition arch temperature

- Flue gas exit temperature

The following needs to be checked every shift for side-mounted level controls:

- Blow down to check that boiler trips and locks-out at extra low water level

### RECOMMENDATIONS

- Ensure that boiler operators measure and record all the above readings.

# BOILER EQUIPMENT

## GRIT COLLECTOR

### FINDINGS

- The grit collector and boiler are not fitted with differential pressure gauges.

- The pressure drop across the grit collector was 680 Pa.

- The grit collector cyclone swirler vanes are likely damaged.

- The grit collector internals and cones are likely eroded/damaged.

- The grit collector double-flap is still in manual control.

- The seal between the grit collector wedge plate and the grit trolley leaks.

### RECOMMENDATIONS

- Clean out the grit collector.

- Install differential pressure gauges on the grit collector and boiler to indicate the level of fouling of the grit collector and boiler.

- Replace the grit collector internals.

- Re-align the grit collector wedge plate so that it seals tightly onto the grit trolley to prevent air entering though bottom of collector which reduces the efficiency of grit collection.

- Emission test to be completed.

# EFFICIENCY

No efficiency test could be done as there were no instruments installed to take any measurements.

Generally, the instrumentation required to complete an efficiency test is as follows:

- Flue gas exit temperature gauge

- Flue gas oxygen content

- Feed water flow meter

- Boiler pressure gauge

- Feed water temperature gauge

# RECOMMENDATIONS

The recommendations for each aspect audited can be found in the relevant clauses above. It is recommended that changes to the plant are implemented in the following priority.

## High Priority

- Replace the stoker.

- Clean the boiler.

- Clean the grit collector.

- Replace the grit collector.

- Install differential pressure gauges on the boiler and the grit collector.

- Arrange a 3-yearly statutory inspection with an AIA.

- Automate the coal handling.

- Replace the boiler control panel with the latest OEM supplied panel.

- Install new feedwater pumps with pipework.

- Obtain a copy of the boiler operating and maintenance manual.

- Repair all steam leaks.

- Repair all water leaks.

- Arrange operator training.

- Arrange maintenance training.

- Replace water level controllers and limiters.

- Replace cables on water level controllers and limiters.

- Replace integral pipework.

- Replace pressure limiter.

- Implement modulating water level control.

- Replace sootblowers.

## Medium Priority

- Replace the insulation on the boiler shell.

- Install Yokogawa furnace draught transmitter.

- Replace sight glass with Klinger reflex gauges.

- Service steam trap sets.

- Implement the recovery and utilisation of available condensate.

- Record flue gas oxygen content.

- Install automated TDS control with sample cooler.

- Calibrate pressure gauges.

- Replace ash trolleys.

- Check grit collector double flap valve operation and internals.

- Automate the operation of the coal screws.

- Automate the soot blowers.

- Automate the coal handling.

- Upgrade the grit collector to the latest 250 mg/nm3.

## Low Priority

- Install side secondary air to reduce smoke formation and reduce particulate emissions.

- Install spiral tubing in the second pass to improve the boiler efficiency.

- Procure a spare set of valves.

| Daily |  | Weekly |  | Monthly |  | Quarterly |  | Yearly |  | Shutdown |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Blowdown gauge glass |  | Test safety valves |  | Clean feed pump suction strainer |  | Test all safety interlocks |  | Check feedwater pump |  | Clean firetubes |  |
| Test feedwater controls |  |  |  | Inspect refractory and insulation |  | Inspect smokebox joints |  |  |  | Clean furnace tube, reversal chamber and tubeplates |  |
| Check O2 content of flue gases |  |  |  |  |  |  |  |  |  | Clean waterside |  |
| Periodic Inspection and Testing |  |  |  | Statutory internal and external inspection and hydraulic test |  |  |  |  |  |  |  |

| ADDITIONAL QUARTERLY CHECKS |  | Mechanical |  |  | Electrical |  |  | Combustion Equipment |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Smokebox doors tight | Safety valve flanges tight | Blowdown valve flanges tight & effortless action |  | Lagging and cladding intact |  | Visual inspection for hotspots |  |  | Main isolator switch functional |  |  |
| Manhole tight | Gauge glasses not leaking | Rear sight glass clean |  | De-ashing door secure |  | Instrumentation connections secure in panel |  |  | All switches/pushbuttons on panel operational |  |  |
| Handholes secure | Feed check valve flanges tight | Ladders and platform secure |  | All panels clean and free of marks, scratches |  | Control circuit correct |  |  | Safety interlocks checked |  |  |
| Safety valve blow off/reset | Cut-out below AWL | High/low O2 settings |  | Fan vibration |  | Flue gas temperature |  |  | Inspect grit collector flap valve and grit trolley |  |  |
| Low water alarm below AWL | Water level height of water column | Pressure controller |  | Smoke output |  | Door bolts tightened |  |  | Inspect ash removal valve and trolley |  |  |

# Appendix A

Maintenance Schedules - Boiler

Maintenance Schedules - Stoker

| Daily |  | Weekly |  | Monthly |  | Quarterly |  | Yearly |  | Shutdown |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Check for broken links |  | Check tension |  | Inspect refractory |  | Inspect refractory |  | Inspect stoker drive oil level |  | Inspect frame |  |
| Check for lack of tension |  | Check guillotine door height |  | Inspect side seals |  |  |  |  |  | Inspect side rear roller |  |
| Check for misalignment or overheating |  |  |  |  |  |  |  |  |  |  |  |
| Check for oil leaks |  |  |  |  |  |  |  |  |  |  |  |
| Periodic Inspection and Testing |  |  |  |  |  |  |  |  |  |  |  |

John Thompson boilers are designed for the following coal specifications.

# Typical Analysis for Coal Grade A Peas

# Ultimate Analysis                 % by Mass

Moisture						2,50

Ash							12,83

Carbon						69,79

Hydrogen						4,10

Nitrogen						1,64

Sulphur							0,62

Oxygen						8,52

##### Proximate Analysis*			% by Mass

Moisture						2,50

Ash							12,83

Volatile Matter						24,63

Fixed Carbon						60,04

Gross Calorific Value MJ/kg				28,50

*Air Dried Basis

Ash Fusion Temperatures		       oC

Deformation	+ 1 400

Hemispherical	+ 1 400

Flow	+ 1 400

Swelling Index		1

# Size Grading 	                                   %

Size range (mm)					% in range

+ 25							  0

- 25 to + 19						15

- 19 to +13						25

- 13 to + 6						43

-   6 to + 3						13

-   3 to + 1						  4

-   1							  1

# Typical Analysis for Coal Grade C Smalls

# Ultimate Analysis            % by Mass

Moisture						2,70

Ash							18,22

Carbon						65,03

Hydrogen						3,43

Nitrogen						1,70

Sulphur							0,66

Oxygen						8,26

##### Proximate Analysis*			% by Mass

Moisture						2,70

Ash							18,22

Volatile Matter						24,84

Fixed Carbon						54,24

Gross Calorific Value MJ/kg				26,00

*Air Dried Basis

# Ash Fusion Temperatures                  °C

Deformation	+ 1 400

Hemispherical	+ 1 400

Flow	+ 1 400

Swelling Index		1

# Size Grading	                           %

Size range (mm)				% in range

+ 25						0

- 25 to + 19					4

- 19 to +13					11

- 13 to + 6					30

-   6 to + 3					25

-   3 to + 1					20

-   1						10